Designation: D149 – 09

An American National Standard

Standard Test Method for

Dielectric Breakdown Voltage and Dielectric Strength of

Solid Electrical Insulating Materials at Commercial Power

Frequencies1

This standard is issued under the ﬁxed designation D149; the number immediately following the designation indicates the year of

original adoption or, in the case of revision, the year of last revision. A number in parentheses indicates the year of last reapproval. A

superscript epsilon (´) indicates an editorial change since the last revision or reapproval.

This standard has been approved for use by agencies of the Department of Defense.

1. Scope*

1.1 This test method covers procedures for the determina-

tion of dielectric strength of solid insulating materials at

commercial power frequencies, under speciﬁed conditions.2,3

1.2 Unless otherwise speciﬁed, the tests shall be made at 60

Hz. However, this test method is suitable for use at any

frequency from 25 to 800 Hz. At frequencies above 800 Hz,

dielectric heating is a potential problem.

1.3 This test method is intended to be used in conjunction

with any ASTM standard or other document that refers to this

test method. References to this document need to specify the

particular options to be used (see 5.5).

1.4 It is suitable for use at various temperatures, and in any

suitable gaseous or liquid surrounding medium.

1.5 This test method is not intended for measuring the

dielectric strength of materials that are ﬂuid under the condi-

tions of test.

1.6 This test method is not intended for use in determining

intrinsic dielectric strength, direct-voltage dielectric strength,

or thermal failure under electrical stress (see Test Method

D3151).

1.7 This test method is most commonly used to determine

the dielectric breakdown voltage through the thickness of a test

specimen (puncture). It is also suitable for use to determine

dielectric breakdown voltage along the interface between a

solid specimen and a gaseous or liquid surrounding medium

(ﬂashover). With the addition of instructions modifying Sec-

tion 12, this test method is also suitable for use for proof

testing.

This test method is under the jurisdiction of ASTM Committee D09 on

Electrical and Electronic Insulating Materials and is the direct responsibility of

Subcommittee D09.12 on Electrical Tests.

Current edition approved Oct. 1, 2009. Published November 2009. Originally

approved in 1922. Last previous edition approved in 2004 as D149 – 97a(2004).

DOI: 10.1520/D0149-09.

2Bartnikas, R., Chapter 3, “High Voltage Measurements,” Electrical Proper-

ties of Solid Insulating Materials, Measurement Techniques , Vol. IIB, Engineering

Dielectrics, R. Bartnikas, Editor, ASTM STP 926, ASTM, Philadelphia, 1987 .

3Nelson, J. K., Chapter 5, “Dielectric Breakdown of Solids,” Electrical

Properties of Solid Insulating Materials: Molecular Structure and Electrical

Behavior, Vol. IIA, Engineering Dielectrics, R. Bartnikas and R. M. Eichorn,

Editors, ASTM STP 783, ASTM, Philadelphia, 1983

1

1.8 This test method is similar to IEC Publication 243-1. All

procedures in this method are included in IEC 243-1. Differ-

ences between this method and IEC 243-1 are largely editorial.

1.9 This standard does not purport to address all of the

safety concerns, if any, associated with its use. It is the

responsibility of the user of this standard to establish appro-

priate safety and health practices and determine the applica-

bility of regulatory limitations prior to use. Speciﬁc hazard

statements are given in Section 7. Also see 6.4.1.

2. Referenced Documents

2.1 ASTM Standards:4

D374 Test Methods for Thickness of Solid Electrical Insu-

lation

D618 Practice for Conditioning Plastics for Testing

D877 Test Method for Dielectric Breakdown Voltage of

Insulating Liquids Using Disk Electrodes

D1711 Terminology Relating to Electrical Insulation

D2413 Practice for Preparation of Insulating Paper and

Board Impregnated with a Liquid Dielectric

D3151 Test Method for Thermal Failure of Solid Electrical

Insulating Materials Under Electric Stress5

D3487 Speciﬁcation for Mineral Insulating Oil Used in

Electrical Apparatus

D5423 Speciﬁcation for Forced-Convection Laboratory

Ovens for Evaluation of Electrical Insulation

2.2 IEC Standard:

Pub. 243-1 Methods of Test for Electrical Strength of Solid

Insulating Materials—Part 1: Tests at Power Frequencies6

For referenced ASTM standards, visit the ASTM website, www.astm.org, or

contact ASTM Customer Service at service@astm.org. For Annual Book of ASTM

Standards volume information, refer to the standard’s Document Summary page on

the ASTM website.

5Withdrawn. The last approved version of this historical standard is referenced

on www.astm.org.

6Available from International Electrotechnical Commission (IEC), 3 rue de

Varembé, Case postale 131, CH-1211, Geneva 20, Switzerland, http://www.iec.ch.

4

*A Summary of Changes section appears at the end of this standard.

Copyright (C) ASTM International, 100 Barr Harbour Dr. P.O. box C-700 West Conshohocken, Pennsylvania 19428-2959, United States

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

D149 – 09

2.3 ANSI Standard:

C68.1 Techniques for Dielectric Tests, IEEE Standard No.

47

3. Terminology

3.1 Deﬁnitions:

3.1.1 dielectric breakdown voltage (electric breakdown

voltage), n—the potential difference at which dielectric failure

occurs under prescribed conditions in an electrical insulating

material located between two electrodes. (See also Appendix

X1.)

3.1.1.1 Discussion—The term dielectric breakdown voltage

is sometimes shortened to “breakdown voltage.”

3.1.2 dielectric failure (under test), n—an event that is

evidenced by an increase in conductance in the dielectric under

test limiting the electric ﬁeld that can be sustained.

3.1.3 dielectric strength, n—the voltage gradient at which

dielectric failure of the insulating material occurs under spe-

ciﬁc conditions of test.

3.1.4 electric strength, n—see dielectric strength.

3.1.4.1 Discussion—Internationally, “electric strength” is

used almost universally.

3.1.5 ﬂashover, n—a disruptive electrical discharge at the

surface of electrical insulation or in the surrounding medium,

which may or may not cause permanent damage to the

insulation.

3.1.6 For deﬁnitions of other terms relating to solid insulat-

ing materials, refer to Terminology D1711.

4. Summary of Test Method

4.1 Alternating voltage at a commercial power frequency

(60 Hz, unless otherwise speciﬁed) is applied to a test

specimen. The voltage is increased from zero or from a level

well below the breakdown voltage, in one of three prescribed

methods of voltage application, until dielectric failure of the

test specimen occurs.

4.2 Most commonly, the test voltage is applied using simple

test electrodes on opposite faces of specimens. The options for

the specimens are that they be molded or cast, or cut from ﬂat

sheet or plate. Other electrode and specimen conﬁgurations are

also suitable for use to accommodate the geometry of the

sample material, or to simulate a speciﬁc application for which

the material is being evaluated.

5. Signiﬁcance and Use

5.1 The dielectric strength of an electrical insulating mate-

rial is a property of interest for any application where an

electrical ﬁeld will be present. In many cases the dielectric

strength of a material will be the determining factor in the

design of the apparatus in which it is to be used.

5.2 Tests made as speciﬁed herein are suitable for use to

provide part of the information needed for determining suit-

ability of a material for a given application; and also, for

detecting changes or deviations from normal characteristics

resulting from processing variables, aging conditions, or other

7

manufacturing or environmental situations. This test method is

useful for process control, acceptance or research testing.

5.3 Results obtained by this test method can seldom be used

directly to determine the dielectric behavior of a material in an

actual application. In most cases it is necessary that these

results be evaluated by comparison with results obtained from

other functional tests or from tests on other materials, or both,

in order to estimate their signiﬁcance for a particular material.

5.4 Three methods for voltage application are speciﬁed in

Section 12: Method A, Short-Time Test; Method B, Step-by-

Step Test; and Method C, Slow Rate-of-Rise Test. Method A is

the most commonly-used test for quality-control tests. How-

ever, the longer-time tests, Methods B and C, which usually

will give lower test results, will potentially give more mean-

ingful results when different materials are being compared with

each other. If a test set with motor-driven voltage control is

available, the slow rate-of-rise test is simpler and preferable to

the step-by-step test. The results obtained from Methods B and

C are comparable to each other.

5.5 Documents specifying the use of this test method shall

also specify:

5.5.1 Method of voltage application,

5.5.2 Voltage rate-of-rise, if slow rate-of-rise method is

speciﬁed,

5.5.3 Specimen selection, preparation, and conditioning,

5.5.4 Surrounding medium and temperature during test,

5.5.5 Electrodes,

5.5.6 Wherever possible, the failure criterion of the current-

sensing element, and

5.5.7 Any desired deviations from the recommended proce-

dures as given.

5.6 If any of the requirements listed in 5.5 are missing from

the specifying document, then the recommendations for the

several variables shall be followed.

5.7 Unless the items listed in 5.5 are speciﬁed, tests made

with such inadequate reference to this test method are not in

conformance with this test method. If the items listed in 5.5 are

not closely controlled during the test, it is possible that the

precisions stated in 15.2 and 15.3 will not be obtained.

5.8 Variations in the failure criteria (current setting and

response time) of the current sensing element signiﬁcantly

affect the test results.

5.9 Appendix X1. contains a more complete discussion of

the signiﬁcance of dielectric strength tests.

6. Apparatus

6.1 Voltage Source—Obtain the test voltage from a step-up

transformer supplied from a variable sinusoidal low-voltage

source. The transformer, its voltage source, and the associated

controls shall have the following capabilities:

6.1.1 The ratio of crest to root-mean-square (rms) test

voltage shall be equal to =2 6 5 % (1.34 to 1.48), with the

test specimen in the circuit, at all voltages greater than 50 % of

the breakdown voltage.

6.1.2 The capacity of the source shall be sufficient to

maintain the test voltage until dielectric breakdown occurs. For

most materials, using electrodes similar to those shown in

Table 1, an output current capacity of 40 mA is usually

satisfactory. For more complex electrode structures, or for

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

Available from American National Standards Institute (ANSI), 25 W. 43rd St.,

4th Floor, New York, NY 10036, http://www.ansi.org.

D149 – 09

TABLE 1 Typical Electrodes for Dielectric Strength Testing of Various Types of Insulating MaterialsA

Electrode

Type

1

2

3

Description of ElectrodesB,C

Opposing cylinders 51 mm (2 in.) in diameter, 25 mm (1 in.) thick with

edges rounded to 6.4 mm (0.25 in.) radius

Opposing cylinders 25 mm (1 in.) in diameter, 25 mm (1 in.) thick with

edges rounded to 3.2 mm (0.125 in.) radius

Opposing cylindrical rods 6.4 mm (0.25 in.) in diameter with edges

rounded to 0.8 mm (0.0313 in.) radiusD

Flat plates 6.4 mm (0.25 in.) wide and 108 mm (4.25 in.) long with edges

square and ends rounded to 3.2 mm (0.125 in.) radius

Hemispherical electrodes 12.7 mm (0.5 in.) in diameterE

Opposing cylinders; the lower one 75 mm (3 in.) in diameter, 15 mm

(0.60 in.) thick; the upper one 25 mm (1 in.) in diameter, 25 mm

thick; with edges of both rounded to 3 mm (0.12 in.) radiusF

Opposing circular ﬂat plates, 150 mm diameterG, 10 mm thick with

edges rounded to 3 to 5 mm radiusH

Insulating Materials

ﬂat sheets of paper, ﬁlms, fabrics, rubber, molded plastics, laminates,

boards, glass, mica, and ceramic

same as for Type 1, particularly for glass, mica, plastic, and ceramic

same as for Type 1, particularly for varnish, plastic, and other thin ﬁlm and

tapes: where small specimens necessitate the use of smaller electrodes,

or where testing of a small area is desired

same as for Type 1, particularly for rubber tapes and other narrow widths

of thin materials

ﬁlling and treating compounds, gels and semisolid compounds and greases,

embedding, potting, and encapsulating materials

same as for Types 1 and 2

4

5

6

7

A

ﬂat sheet, plate, or board materials, for tests with the voltage gradient

parallel to the surface

These electrodes are those most commonly speciﬁed or referenced in ASTM standards. With the exception of Type 5 electrodes, no attempt has been made to suggest

electrode systems for other than ﬂat surface material. It is acceptable to use other electrodes as speciﬁed in ASTM standards or as agreed upon between seller and

purchaser where none of these electrodes in the table is suitable for proper evaluation of the material being tested.

BElectrodes are normally made from either brass or stainless steel. Reference shall be made to the standard governing the material to be tested to determine which,

if either, material is preferable.

CThe electrodes surfaces shall be polished and free from irregularities resulting from previous testing.

DRefer to the appropriate standard for the load force applied by the upper electrode assembly. Unless otherwise speciﬁed the upper electrodes shall be 50 6 2 g.

ERefer to the appropriate standard for the proper gap settings.

FThe Type 6 electrodes are those given in IEC Publication 243-1 for testing of ﬂat sheet materials. They are less critical as to concentricity of the electrodes than are

the Types 1 and 2 electrodes.

GIt is acceptable to use other diameters, provided that all parts of the test specimen are at least 15 mm inside the edges of the electrodes.

HThe Type 7 electrodes, as described in the table and in NoteG, are those given in IEC Publication 243-1 for making tests parallel to the surface.

testing high-loss materials, it is possible that higher current

capacity will be needed. The power rating for most tests will

vary from 0.5 kVA for testing low-capacitance specimens at

voltages up to 10 kV, to 5 kVA for voltages up to 100 kV.

6.1.3 The controls on the variable low-voltage source shall

be capable of varying the supply voltage and the resultant test

voltage smoothly, uniformly, and without overshoots or tran-

sients, in accordance with 12.2. Do not allow the peak voltage

to exceed 1.48 times the indicated rms test voltage under any

circumstance. Motor-driven controls are preferable for making

short-time (see 12.2.1) or slow-rate-of-rise (see 12.2.3) tests.

6.1.4 Equip the voltage source with a circuit-breaking

device that will operate within three cycles. The device shall

disconnect the voltage-source equipment from the power

service and protect it from overload as a result of specimen

breakdown causing an overload of the testing apparatus. If

prolonged current follows breakdown it will result in unnec-

essary burning of the test specimens, pitting of the electrodes,

and contamination of any liquid surrounding medium.

6.1.5 It is important for the circuit-breaking device to have

an adjustable current-sensing element in the step-up trans-

former secondary, to allow for adjustment consistent with the

specimen characteristics and arranged to sense specimen cur-

rent. Set the sensing element to respond to a current that is

indicative of specimen breakdown as deﬁned in 12.3.

6.1.6 The current setting is likely to have a signiﬁcant effect

on the test results. Make the setting high enough that transients,

such as partial discharges, will not trip the breaker but not so

high that excessive burning of the specimen, with resultant

electrode damage, will occur on breakdown. The optimum

current setting is not the same for all specimens and depending

upon the intended use of the material and the purpose of the

test, it is often desirable to make tests on a given sample at

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

more than one current setting. The electrode area is likely to

have a signiﬁcant effect upon the choice of current setting.

6.1.7 It is possible that the specimen current-sensing ele-

ment will be in the primary of the step-up transformer.

Calibrate the current-sensing dial in terms of specimen current.

6.1.8 Exercise care in setting the response of the current

control. If the control is set too high, the circuit will not

respond when breakdown occurs; if set too low, it is possible

that it will respond to leakage currents, capacitive currents, or

partial discharge (corona) currents or, when the sensing ele-

ment is located in the primary, to the step-up transformer

magnetizing current.

6.2 Voltage Measurement—A voltmeter must be provided

for measuring the rms test voltage. If a peak-reading voltmeter

is used, divide the reading by =2 to get rms values. The

overall error of the voltage-measuring circuit shall not exceed

5 % of the measured value. In addition, the response time of

the voltmeter shall be such that its time lag will not be greater

than 1 % of full scale at any rate-of-rise used.

6.2.1 Measure the voltage using a voltmeter or potential

transformer connected to the specimen electrodes, or to a

separate voltmeter winding, on the test transformer, that is

unaffected by the step-up transformer loading.

6.2.2 It is desirable for the reading of the maximum applied

test voltage to be retained on the voltmeter after breakdown so

that the breakdown voltage can be accurately read and re-

corded.

6.3 Electrodes—For a given specimen conﬁguration, it is

possible that the dielectric breakdown voltage will vary con-

siderably, depending upon the geometry and placement of the

test electrodes. For this reason it is important that the elec-

trodes to be used be described when specifying this test

method, and that they be described in the report.

D149 – 09

6.3.1 One of the electrodes listed in Table 1 shall be

speciﬁed by the document referring to this test method. If no

electrodes have been speciﬁed, select an applicable one from

Table 1, or use other electrodes mutually acceptable to the

parties concerned when the standard electrodes cannot be used

due to the nature or conﬁguration of the material being tested.

See references in Appendix X2 for examples of some special

electrodes. In any event the electrodes must be described in the

report.

6.3.2 The electrodes of Types 1 through 4 and Type 6 of

Table 1 shall be in contact with the test specimen over the

entire ﬂat area of the electrodes.

6.3.3 The specimens tested using Type 7 electrodes shall be

of such size that all portions of the specimen will be within and

no less than 15 mm from the edges of the electrodes during

test. In most cases, tests using Type 7 electrodes are made with

the plane of the electrode surfaces in a vertical position. Tests

made with horizontal electrodes shall not be directly compared

with tests made with vertical electrodes, particularly when the

tests are made in a liquid surrounding medium.

6.3.4 Keep the electrode surfaces clean and smooth, and

free from projecting irregularities resulting from previous tests.

If asperities have developed, they must be removed.

6.3.5 It is important that the original manufacture and

subsequent resurfacing of electrodes be done in such a manner

that the speciﬁed shape and ﬁnish of the electrodes and their

edges are maintained. The ﬂatness and surface ﬁnish of the

electrode faces must be such that the faces are in close contact

with the test specimen over the entire area of the electrodes.

Surface ﬁnish is particularly important when testing very thin

materials which are subject to physical damage from improp-

erly ﬁnished electrodes. When resurfacing, do not change the

transition between the electrode face and any speciﬁed edge

radius.

6.3.6 Whenever the electrodes are dissimilar in size or

shape, ensure that the one at which the lowest concentration of

stress exists, usually the larger in size and with the largest

radius, is at ground potential.

6.3.7 In some special cases liquid metal electrodes, foil

electrodes, metal shot, water, or conductive coating electrodes

are used. It must be recognized that it is possible that these will

give results differing widely from those obtained with other

types of electrodes.

6.3.8 Because of the effect of the electrodes on the test

results, it is frequently possible to obtain additional informa-

tion as to the dielectric properties of a material (or a group of

materials) by running tests with more than one type of

electrode. This technique is of particular value for research

testing.

6.4 Surrounding Medium—The document calling for this

test method needs to specify the surrounding medium and the

test temperature. Since ﬂashover must be avoided and the

effects of partial discharges prior to breakdown mimimized,

even for short time tests, it is often preferable and sometimes

necessary to make the tests in insulating liquid (see 6.4.1).

Breakdown values obtained in insulating liquid are often not

comparable with those obtained in air. The nature of the

insulating liquid and the degree of previous use are factors

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

inﬂuencing the test values. In some cases, testing in air will

require excessively large specimens or cause heavy surface

discharges and burning before breakdown. Some electrode

systems for testing in air make use of pressure gaskets around

the electrodes to prevent ﬂashover. The material of the gaskets

or seals around the electrodes has the potential to inﬂuence the

breakdown values.

6.4.1 When tests are made in insulating oil, an oil bath of

adequate size shall be provided. (Warning—The use of glass

containers is not recommended for tests at voltages above

about 10 kV, because the energy released at breakdown has the

potential to be sufficient to shatter the container. Metal baths

must be grounded.)

It is recommended that mineral oil meeting the requirements

of Speciﬁcation D3487, Type I or II, be used. It shall have a

dielectric breakdown voltage as determined by Test Method

D877 of at least 26 kV. Other dielectric ﬂuids are suitable for

use as surrounding mediums if speciﬁed. These include, but are

not limited to, silicone ﬂuids and other liquids intended for use

in transformers, circuit breakers, capacitors, or cables.

6.4.1.1 The quality of the insulating oil has the potential to

have an appreciable effect upon the test results. In addition to

the dielectric breakdown voltage, mentioned above, particulate

contaminants are especially important when very thin speci-

mens (25 µm (1 mil) or less) are being tested. Depending upon

the nature of the oil and the properties of the material being

tested, other properties, including dissolved gas content, water

content, and dissipation factor of the oil also have the potential

to affect the results. Frequent replacement of the oil, or the use

of ﬁlters and other reconditioning equipment is important to

minimize the effect of variations of the quality of the oil on the

test results.

6.4.1.2 Breakdown values obtained using liquids having

different electrical properties are often not comparable. (See

X1.4.7.) If tests are to be made at other than room temperature,

the bath must be provided with a means for heating or cooling

the liquid, and with a means to ensure uniform temperature.

Small baths can in some cases be placed in an oven (see 6.4.2)

in order to provide temperature control. If forced circulation of

the ﬂuid is provided, care must be taken to prevent bubbles

from being whipped into the ﬂuid. The temperature shall be

maintained within 65°C of the speciﬁed test temperature at the

electrodes, unless otherwise speciﬁed. In many cases it is

speciﬁed that specimens to be tested in insulating oil are to be

previously impregnated with the oil and not removed from the

oil before testing (see Practice D2413). For such materials, the

bath must be of such design that it will not be necessary to

expose the specimens to air before testing.

6.4.2 If tests in air are to be made at other than ambient

temperature or humidity, an oven or controlled humidity

chamber must be provided for the tests. Ovens meeting the

requirements of Speciﬁcation D5423 and provided with means

for introducing the test voltage will be suitable for use when

only temperature is to be controlled.

6.4.3 Tests in gasses other than air will generally require the

use of chambers that can be evacuated and ﬁlled with the test

gas, usually under some controlled pressure. The design of

D149 – 09

such chambers will be determined by the nature of the test

program to be undertaken.

6.5 Test Chamber—The test chamber or area in which the

tests are to be made shall be of sufficient size to hold the test

equipment, and shall be provided with interlocks to prevent

accidental contact with any electrically energized parts. A

number of different physical arrangements of voltage source,

measuring equipment, baths or ovens, and electrodes are

possible, but it is essential that (1) all gates or doors providing

access to spaces in which there are electrically energized parts

be interlocked to shut off the voltage source when opened; ( 2)

clearances are sufficiently large that the ﬁeld in the area of the

electrodes and specimen are not distorted and that ﬂashovers

and partial discharges (corona) do not occur except between

the test electrodes; and (3) insertion and replacement of

specimens between tests be as simple and convenient as

possible. Visual observation of the electrodes and test specimen

during the test is frequently desirable.

7. Hazards

7.1 Warning—It is possible that lethal voltages will be

present during this test. It is essential that the test apparatus,

and all associated equipment electrically connected to it, be

properly designed and installed for safe operation. Solidly

ground all electrically conductive parts that any person might

come into contact with during the test. Provide means for use

at the completion of any test to ground any parts which fall into

any of the following cases: (a) were at high voltage during the

test; (b) have the potential to acquire an induced charge during

the test; or (c) have the potential to retain a charge even after

disconnection of the voltage source. Thoroughly instruct all

operators in the proper way to conduct tests safely. When

making high-voltage tests, particularly in compressed gas or in

oil, it is possible that the energy released at breakdown will be

sufficient to result in ﬁre, explosion, or rupture of the test

chamber. Design test equipment, test chambers, and test

specimens so as to minimize the possibility of such occur-

rences and to eliminate the possibility of personal injury.

7.2 Warning—Ozone is a physiologically hazardous gas at

elevated concentrations. The exposure limits are set by gov-

ernmental agencies and are usually based upon recommenda-

tions made by the American Conference of Governmental

Industrial Hygienists.8 Ozone is likely to be present whenever

voltages exist which are sufficient to cause partial, or complete,

discharges in air or other atmospheres that contain oxygen.

Ozone has a distinctive odor which is initially discernible at

low concentrations but sustained inhalation of ozone can cause

temporary loss of sensitivity to the scent of ozone. Because of

this it is important to measure the concentration of ozone in the

atmosphere, using commercially available monitoring devices,

whenever the odor of ozone is persistently present or when

ozone generating conditions continue. Use appropriate means,

such as exhaust vents, to reduce ozone concentrations to

acceptable levels in working areas.

8. Sampling

8.1 The detailed sampling procedure for the material being

tested needs to be deﬁned in the speciﬁcation for that material.

8.2 Sampling procedures for quality control purposes shall

provide for gathering of sufficient samples to estimate both the

average quality and the variability of the lot being examined;

and for proper protection of the samples from the time they are

taken until the preparation of the test specimens in the

laboratory or other test area is begun.

8.3 For the purposes of most tests it is desirable to take

samples from areas that are not immediately adjacent to

obvious defects or discontinuities in the material. Avoid the

outer few layers of roll material, the top sheets of a package of

sheets, or material immediately next to an edge of a sheet or

roll, unless the presence or proximity of defects or disconti-

nuities is of interest in the investigation of the material.

8.4 The sample shall be large enough to permit making as

many individual tests as required for the particular material

(see 12.4).

9. Test Specimens

9.1 Preparation and Handling:

9.1.1 Prepare specimens from samples collected in accor-

dance with Section 8.

9.1.2 When ﬂat-faced electrodes are to be used, the surfaces

of the specimens which will be in contact with the electrodes

shall be smooth parallel planes, insofar as possible without

actual surface machining.

9.1.3 The specimens shall be of sufficient size to prevent

ﬂashover under the conditions of test. For thin materials it will

often be convenient to use specimens large enough to permit

making more than one test on a single piece.

9.1.4 For thicker materials (usually more than 2 mm thick)

it is possible that the breakdown strength will be high enough

that ﬂashover or intense surface partial discharges (corona) will

occur prior to breakdown. Techniques that are suitable for use

to prevent ﬂashover, or to reduce partial discharge (corona)

include:

9.1.4.1 Immerse the specimen in insulating oil during the

test. See X1.4.7 for the surrounding medium factors inﬂuenc-

ing breakdown. This is often necessary for specimens that have

not been dried and impregnated with oil, as well as for those

which have been prepared in accordance with Practice D2413,

for example. (See 6.4.)

9.1.4.2 Machine a recess or drill a ﬂat-bottom hole in one or

both surfaces of the specimen to reduce the test thickness. If

dissimilar electrodes are used (such as Type 6 of Table 1) and

only one surface is to be machined, the larger of the two

electrodes shall be in contact with the machined surface. Care

must be taken in machining specimens not to contaminate or

mechanically damage them.

9.1.4.3 Apply seals or shrouds around the electrodes, in

contact with the specimen to reduce the tendency to ﬂashover.

9.1.5 Materials that are not in ﬂat sheet form shall be tested

using specimens (and electrodes) appropriate to the material

and the geometry of the sample. It is essential that for these

materials both the specimen and the electrodes be deﬁned in

the speciﬁcation for the material.

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

Available from American Conference of Governmental Industrial Hygienists,

Inc. (ACGIH), 1330 Kemper Meadow Dr., Cincinnati, OH 45240, http://

www.acgih.org.

8

D149 – 09

9.1.6 Whatever the form of the material, if tests of other

than surface-to-surface puncture strength are to be made,

deﬁne the specimens and the electrodes in the speciﬁcation for

the material.

9.2 In nearly all cases the actual thickness of the test

specimen is important. Unless otherwise speciﬁed, measure the

thickness after the test in the immediate vicinity of the area of

breakdown. Measurements shall be made at room temperature

(25 6 5°C), using the appropriate procedure of Test Methods

D374.

10. Calibration

10.1 In making calibration measurements, take care that the

values of voltage at the electrodes can be determined within the

accuracy given in 6.2, with the test specimens in the circuit.

10.2 Use an independently calibrated voltmeter attached to

the output of the test voltage source to verify the accuracy of

the measuring device. Examples of such voltmeters suitable for

calibration measurement are: electrostatic voltmeters, voltage

dividers, or potential transformers having comparable accu-

racy.

10.3 At voltages above about 12 kV rms (16.9 kV peak) a

sphere gap is suitable for use to calibrate the readings of the

voltage-measuring device. Follow procedures as speciﬁed in

ANSI C68.1 in such calibration.

11. Conditioning

11.1 The dielectric strength of most solid insulating mate-

rials is inﬂuenced by temperature and moisture content. Mate-

rials so affected shall be brought to equilibrium with an

atmosphere of controlled temperature and relative humidity

before testing. For such materials, the conditioning shall be

included in the standard referencing this test method.

11.2 Unless otherwise speciﬁed, follow the procedures in

Practice D618.

11.3 For many materials the moisture content has more

effect on dielectric strength than does temperature. Condition-

ing times for these materials shall be sufficiently long to permit

the specimens to reach moisture equilibrium as well as

temperature equilibrium.

11.4 If the conditioning atmosphere is such that condensa-

tion occurs on the surface of the specimens, it is often desirable

to wipe the surfaces of the specimens immediately before

testing. This will usually reduce the probability of surface

ﬂashover.

12. Procedure

12.1 (Warning—see Section 7 before commencement of

any test.)

12.2 Methods of Voltage Application:

12.2.1 Method A, Short-Time Test—Apply voltage uni-

formly to the test electrodes from zero at one of the rates shown

in Fig. 1 until breakdown occurs. Use the short-time test unless

otherwise speciﬁed.

12.2.1.1 When establishing a rate initially in order for it to

be included in a new speciﬁcation, select a rate that, for a given

set of specimens, will give an average time to breakdown of

between 10 and 20 s. In some cases it will be necessary to run

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

Rates

(V/s) 6 20 %

100

200

500

1000

2000

5000

FIG. 1 Voltage Proﬁle of the Short-Time Test

one or two preliminary tests in order to determine the most

suitable rate-of-rise. For many materials a rate of 500 V/s is

used.

12.2.1.2 If the document referencing this test method speci-

ﬁed a rate-of-rise, it shall be used consistently in spite of

occasional average time to breakdown falling outside the range

of 10 to 20 s. In this case, the times to failures shall be made

a part of the report.

12.2.1.3 In running a series of tests comparing different

material, the same rate-of-rise shall be used with preference

given to a rate that allows the average time to be between 10

and 20 s. If the time to breakdown cannot be adhered to, the

time shall be made a part of the report.

12.2.2 Method B, Step-by-Step Test—Apply voltage to the

test electrodes at the preferred starting voltage and in steps and

duration as shown in Fig. 2 until breakdown occurs.

12.2.2.1 From the list in Fig. 2, select the initial voltage, Vs,

to be the one closest to 50 % of the experimentally determined

or expected breakdown voltage under the short time test.

12.2.2.2 If an initial voltage other than one of the preferred

values listed in Fig. 2 is selected, it is recommended that the

voltage steps be 10 % of the preferred initial voltage immedi-

ately below the selected value.

12.2.2.3 Apply the initial voltage by increasing the voltage

from zero as rapidly as can be accomplished without introduc-

ing a peak voltage exceeding that permitted in 6.1.3. Similar

requirements shall apply to the procedure used to increase the

voltage between successive steps. After the initial step, the time

required to raise the voltage to the succeeding step shall be

counted as part of the time at the succeeding step.

12.2.2.4 If breakdown occurs while the voltage is being

increased to the next step, the specimen is described as having

sustained a dielectric withstand voltage, Vws, equal to the

voltage of the step just ended. If breakdown occurs prior to the

end of the holding period at any step, the dielectric withstand

voltage, Vws, for the specimen is taken as the voltage at the last

completed step. The voltage at breakdown, Vbd, is to be used to

calculate dielectric breakdown strength. The dielectric with-

stand strength is to be calculated from the thickness and the

dielectric withstand voltage, Vws. (See Fig. 2.)

D149 – 09

Preferred starting voltages, Vs are 0.25, 0.50, 1, 2, 5, 10, 20, 50, and 100 kV.

Step Voltage

when

Vs(kV)A is

5 or less

over 5 to 10

over 10 to 25

over 25 to 50

over 50 to 100

over 100

A

Increment

(kV)

10 % of Vs

0.50

1

2

5

10

Rates (V/s) 6 20 %

1

2

5

10

12.5

20

25

50

100

Constraints

tbd > 120 s

Vbd = > 1.5 Vs

FIG. 3 Voltage Proﬁle of Slow Rate-of-Rise Test

Vs = 0.5 ( Vbd for Short-Time Test) unless constraints cannot be met.

________________________________________________________________

Constraints

(t 1 − t0) = (t2 − t1) = ... = (60 6 5)s

Alternate step times, (20 6 3)s and (300 6 10)s

120s # tbd # 720s, for 60s steps

________________________________________________________________

FIG. 2 Voltage Proﬁle of Step-by-Step Test

12.2.2.5 It is desirable that breakdown occur in four to ten

steps, but in not less than 120 s. If failure occurs at the third

step or less, or in less than 120 s, whichever is greater, on more

than one specimen in a group, repeat the tests with a lower

initial voltage. If failure does not occur before the twelfth step

or greater than 720 s, increase the initial voltage.

12.2.2.6 Record the initial voltage, the voltage steps, the

breakdown voltage, and the length of time that the breakdown

voltage was held. If failure occurred while the voltage was

being increased to the starting voltage the failure time shall be

zero.

12.2.2.7 It is acceptable for other time lengths for the

voltage steps to be speciﬁed, depending upon the purpose of

the test. Commonly used lengths are 20 s and 300 s (5 min).

For research purposes, in some cases it will be of value to

conduct tests using more than one time interval on a given

material.

12.2.3 Method C, Slow Rate-of-Rise Test—Apply voltage to

the test electrodes, from the starting voltage and at the rate

shown in Fig. 3 until breakdown occurs.

12.2.3.1 Select the initial voltage from short-time tests made

as speciﬁed in 12.2.1. The initial voltage shall be reached as

speciﬁed in 12.2.2.3.

12.2.3.2 Use the rate-of-voltage rise from the initial value

speciﬁed in the document calling for this test method. Ordi-

narily the rate is selected to approximate the average rate for a

step-by-step test.

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

12.2.3.3 If more than one specimen of a group of specimens

breaks down in less than 120 s, reduce either the initial voltage

or the rate-of-rise, or both.

12.2.3.4 If more than one specimen of a group of specimens

breaks down at less than 1.5 times the initial voltage, reduce

the initial value. If breakdown repeatedly occurs at a value

greater than 2.5 times the initial value (and at a time of over

120 s), increase the initial voltage.

12.3 Criteria of Breakdown—Dielectric failure or dielectric

breakdown (as deﬁned in Terminology D1711) consists of an

increase in conductance, limiting the electric ﬁeld that can be

sustained. This phenomenon is most commonly evidenced

during the test by an abrupt visible and audible rupture through

the thickness of the specimen, resulting in a visible puncture

and decomposition of the specimen in the breakdown area.

This form of breakdown is generally irreversible. Repeated

applications of voltage will sometimes result in failure at lower

voltages (sometimes unmeasurably low), usually with addi-

tional damage at the breakdown area. It is acceptable to use

such repeated applications of voltage to give positive evidence

of breakdown and to make the breakdown path more visible.

12.3.1 In some cases a rapid rise in leakage current will

result in tripping of the voltage source without visible decom-

position of the specimen. This type of failure, usually associ-

ated with slow-rise tests at elevated temperatures, will in some

cases be reversible, that is, it is possible that recovery of the

dielectric strength will occur if the specimen is allowed to cool

to its original test temperature before reapplying voltage. The

voltage source must trip rapidly at relatively low current for

this type of failure to occur.

12.3.2 In some cases tripping of the voltage source will

occur due to ﬂashover, to partial discharge current, to reactive

current in a high capacitance specimen, or to malfunctioning of

the breaker. Such interruptions of the test do not constitute

breakdown (except for ﬂashover tests) and shall not be

considered as a satisfactory test.

D149 – 09

12.3.3 If the breaker is set for too high a current, or if the

breaker malfunctions, excessive burning of the specimen will

occur.

12.4 Number of Tests—Make ﬁve breakdowns unless oth-

erwise speciﬁed for the particular material.

13. Calculation

13.1 Calculate for each test the dielectric strength in kV/mm

or V/mil at breakdown, and for step-by-step tests, the gradient

at the highest voltage step at which breakdown did not occur.

13.2 Calculate the average dielectric strength and the stan-

dard deviation, or other measure of variability.

14. Report

14.1 Report the following information:

14.1.1 Identiﬁcation of the test sample.

14.1.2 For Each Specimen:

14.1.2.1 Measured thickness,

14.1.2.2 Maximum voltage withstood (for step-by-step

tests),

14.1.2.3 Dielectric breakdown voltage,

14.1.2.4 Dielectric strength (for step-by-step tests),

14.1.2.5 Dielectric breakdown strength, and

14.1.3.8 Test temperature,

14.1.3.9 Description of electrodes,

14.1.3.10 Method of voltage application,

14.1.3.11 If speciﬁed, the failure criterion of the current-

sensing element, and

14.1.3.12 Date of test.

15. Precision and Bias

15.1 The results of an interlaboratory study with four

laboratories and eight materials are summarized in Table 2.

This study made use of one electrode system and one test

medium.9

15.2 Single-Operator Precision—Depending upon the vari-

ability of the material being tested, the specimen thickness,

method of voltage application, and the extent to which tran-

sient voltage surges are controlled or suppressed, it is possible

that the coefficient of variation (standard deviation divided by

the mean) will vary from a low 1 % to as high as 20 % or more.

When making duplicate tests on ﬁve specimens from the same

sample, the coefficient of variation usually is less than 9 %.

15.3 Multilaboratory Precision—The precision of tests

made in different laboratories (or of tests made using different

TABLE 2 Dielectric StrengthA Data Summary From Four Laboratories

Material

Polyethylene

Terephthalate

Polyethylene

Terephthalate

Fluorinated

Ethylene

Propylene

Fluorinated

Ethylene

Propylene

PETP ﬁber

reinforced

epoxy resin

PETP ﬁber

reinforced

epoxy resin

Epoxy-Glass

Laminate

Crosslinked

Polyethylene

A

Thickness

(in. nom.)

0.001

0.01

0.003

Dielectric Strength (V/mil)

mean

4606

1558

3276

max

5330

1888

3769

min

4100

1169

2167

Standard

Deviation

332

196

333

Coefficient of

Variation (%)

7.2

12.6

10.2

0.005

2530

3040

2140

231

9.1

0.025

956

1071

783

89

9.3

0.060

583

643

494

46

7.9

0.065

0.044

567

861

635

948

489

729

43

48

Average

7.6

5.6

8.7

Tests performed with specimens in oil using Type 2 electrodes (see Table 1).

14.1.2.6 Location of failure (center of electrode, edge, or

outside).

14.1.3 For Each Sample:

14.1.3.1 Average dielectric withstand strength for step-by-

step test specimens only,

14.1.3.2 Average dielectric breakdown strength,

14.1.3.3 Indication of variability, preferably the standard

deviation and coefficient of variation,

14.1.3.4 Description of test specimens,

14.1.3.5 Conditioning and specimen preparation,

14.1.3.6 Ambient atmosphere temperature and relative hu-

midity,

14.1.3.7 Surrounding medium,

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

equipment in the same laboratory) is variable. Using identical

types of equipment and controlling specimen preparation,

electrodes and testing procedures closely, the single-operator

precision is approachable. When making a direct comparison

of results from two or more laboratories, evaluate the precision

between the laboratories.

15.4 If the material under test, the specimen thickness, the

electrode conﬁguration, or the surrounding medium differs

from those listed in Table 1, or if the failure criterion of the

current-sensing element of the test equipment is not closely

9

The complete report is available from ASTM International. Request D09-1026.

D149 – 09

controlled, it is possible that the precisions cited in 15.2 and

15.3 will not be obtained. Standards which refer to this method

need to determine for the material with which that standard is

concerned the applicability of this precision statement to that

particular material. Refer to 5.4-5.8 and 6.1.6.

15.5 Use special techniques and equipment for materials

having a thickness of 0.001 in. or less. The electrodes must not

damage the specimen upon contact. Accurately determine the

voltage at breakdown.

15.6 Bias—This test method does not determine the intrin-

sic dielectric strength. The test values are dependent upon

specimen geometry, electrodes, and other variable factors, in

addition to the properties of the sample, so that it is not

possible to make a statement of bias.

16. Keywords

16.1 breakdown; breakdown voltage; calibration; criteria of

breakdown; dielectric breakdown voltage; dielectric failure;

dielectric strength; electrodes; ﬂashover; power frequency;

process-control testing; proof testing; quality-control testing;

rapid rise; research testing; sampling; slow rate-of-rise; step-

by-step; surrounding medium; voltage withstand

APPENDIXES

(Nonmandatory Information)

X1. SIGNIFICANCE OF THE DIELECTRIC STRENGTH TEST

X1.1 Introduction

X1.1.1 A brief review of three postulated mechanisms of

breakdown, namely: (1) the discharge or corona mechanism,

(2) the thermal mechanism, and (3) the intrinsic mechanism, as

well as a discussion of the principal factors affecting tests on

practical dielectrics, are given here to aid in interpreting the

data. The breakdown mechanisms usually operate in combina-

tion rather than singly. The following discussion applies only to

solid and semisolid materials.

X1.2 Postulated Mechanisms of Dielectric Breakdown

X1.2.1 Breakdown Caused by Electrical Discharges—In

many tests on commercial materials, breakdown is caused by

electrical discharges, which produce high local ﬁelds. With

solid materials the discharges usually occur in the surrounding

medium, thus increasing the test area and producing failure at

or beyond the electrode edge. Discharges may occur in any

internal voids or bubbles that are present or may develop.

These may cause local erosion or chemical decomposition.

These processes may continue until a complete failure path is

formed between the electrodes.

X1.2.2 Thermal Breakdown—Cumulative heating develops

in local paths within many materials when they are subjected to

high electric ﬁeld intensities, causing dielectric and ionic

conduction losses which generate heat more rapidly than can

be dissipated. Breakdown may then occur because of thermal

instability of the material.

X1.2.3 Intrinsic Breakdown—If electric discharges or ther-

mal instability do not cause failure, breakdown will still occur

when the ﬁeld intensity becomes sufficient to accelerate elec-

trons through the material. This critical ﬁeld intensity is called

the intrinsic dielectric strength. It cannot be determined by this

test method, although the mechanism itself may be involved.

X1.3 Nature of Electrical Insulating Materials

X1.3.1 Solid commercial electrical insulating materials are

generally nonhomogeneous and may contain dielectric defects

of various kinds. Dielectric breakdown often occurs in an area

of the test specimen other than that where the ﬁeld intensity is

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

greatest and sometimes in an area remote from the material

directly between the electrodes. Weak spots within the volume

under stress sometimes determine the test results.

X1.4 Inﬂuence of Test and Specimen Conditions

X1.4.1 Electrodes— In general, the breakdown voltage will

tend to decrease with increasing electrode area, this area effect

being more pronounced with thin test specimens. Test results

are also affected by the electrode geometry. Results may be

affected also by the material from which the electrodes are

constructed, since the thermal and discharge mechanism may

be inﬂuenced by the thermal conductivity and the work

function, respectively, of the electrode material. Generally

speaking, the effect of the electrode material is difficult to

establish because of the scatter of experimental data.

X1.4.2 Specimen Thickness—The dielectric strength of

solid commercial electrical insulating materials is greatly

dependent upon the specimen thickness. Experience has shown

that for solid and semi-solid materials, the dielectric strength

varies inversely as a fractional power of the specimen thick-

ness, and there is a substantial amount of evidence that for

relatively homogeneous solids, the dielectric strength varies

approximately as the reciprocal of the square root of the

thickness. In the case of solids that can be melted and poured

to solidify between ﬁxed electrodes, the effect of electrode

separation is less clearly deﬁned. Since the electrode separation

can be ﬁxed at will in such cases, it is customary to perform

dielectric strength tests on liquids and usually on fusible solids,

with electrodes having a standardized ﬁxed spacing. Since the

dielectric strength is so dependent upon thickness it is mean-

ingless to report dielectric strength data for a material without

stating the thickness of the test specimens used.

X1.4.3 Temperature—The temperature of the test specimen

and its surrounding medium inﬂuence the dielectric strength,

although for most materials small variations of ambient tem-

perature may have a negligible effect. In general, the dielectric

strength will decrease with increasing temperatures, but the

extent to which this is true depends upon the material under

test. When it is known that a material will be required to

D149 – 09

function at other than normal room temperature, it is essential

that the dielectric strength-temperature relationship for the

material be determined over the range of expected operating

temperatures.

X1.4.4 Time—Test results will be inﬂuenced by the rate of

voltage application. In general, the breakdown voltage will

tend to increase with increasing rate of voltage application.

This is to be expected because the thermal breakdown mecha-

nism is time-dependent and the discharge mechanism is usually

time-dependent, although in some cases the latter mechanism

may cause rapid failure by producing critically high local ﬁeld

intensitives.

X1.4.5 Wave Form—In general, the dielectric strength is

inﬂuenced by the wave form of the applied voltage. Within the

limits speciﬁed in this method the inﬂuence of wave form is not

signiﬁcant.

X1.4.6 Frequency—The dielectric strength is not signiﬁ-

cantly inﬂuenced by frequency variations within the range of

commercial power frequencies provided for in this method.

However, inferences concerning dielectric strength behavior at

other than commercial power frequencies (50 to 60 Hz) must

not be made from results obtained by this method.

X1.4.7 Surrounding Medium—Solid insulating materials

having a high breakdown voltage are usually tested by immers-

ing the test specimens in a liquid dielectric such as transformer

oil, silicone oil, or chloroﬂuorocarbons, in order to minimize

the effects of surface discharges prior to breakdown. It has been

shown by S. Whitehead10 that in order to avoid discharges in

the surrounding medium prior to reaching the breakdown

voltage of the solid test specimen, in alternating voltage tests it

is necessary that

Em´8m =Dm 2 1 1 . Es´8s =Ds 2 1 1

(X1.1)

X1.4.7.1 Whitehead points out that it is therefore desirable

to increase Em and ´m, or sm, if surface discharges are to be

avoided. Transformer oil is usually speciﬁed and its dielectric

properties are usually such that edge breakdown will generally

occur if the electric strength, Es, approaches the value given

by:

Es 5

S

4.2 63

ts 1 ´8 s kV/mm

D

(X1.4)

In cases of large thickness of specimen and low permittivity

of specimen, the term containing ts becomes relatively insig-

niﬁcant and the product of permittivity and electric strength is

approximately a constant.11 Whitehead also mentions (p. 261)

that the use of moist semiconducting oil can affect an appre-

ciable reduction in edge discharges. Unless the breakdown path

between the electrodes is solely within the solid, results in one

medium cannot be compared with those in a different medium.

It should also be noted that if the solid is porous or capable of

being permeated by the immersion medium, the breakdown

strength of the solid is directly affected by the electrical

properties of immersion medium.

X1.4.8 Relative Humidity—The relative humidity inﬂu-

ences the dielectric strength to the extent that moisture ab-

sorbed by, or on the surface of, the material under test affects

the dielectric loss and surface conductivity. Hence, its impor-

tance will depend to a large extent upon the nature of the

material being tested. However, even materials that absorb

little or no moisture may be affected because of greatly

increased chemical effects of discharge in the presence of

moisture. Except in cases where the effect of exposure on

dielectric strength is being investigated, it is customary to

control or limit the relative humidity effects by standard

conditioning procedures.

X1.5 Evaluation

X1.5.1 A fundamental requirement of the insulation in

electrical apparatus is that it withstand the voltage imposed on

it in service. Therefore there is a great need for a test to

evaluate the performance of particular materials at high voltage

stress. The dielectric breakdown voltage test represents a

convenient preliminary test to determine whether a material

merits further consideration, but it falls short of a complete

evaluation in two important respects. First, the condition of a

material as installed in apparatus is much different from its

condition in this test, particularly with regard to the conﬁgu-

ration of the electric ﬁeld and the area of material exposed to

it, corona, mechanical stress, ambient medium, and association

with other materials. Second, in service there are deteriorating

inﬂuences, heat, mechanical stress, corona and its products,

contaminants, and so forth, which may reduce the breakdown

voltage far below its value as originally installed. Some of

these effects can be incorporated in laboratory tests, and a

better estimate of the material will result, but the ﬁnal

consideration must always be that of the performance of the

material in actual service.

Starr, R. W., “Dielectric Materials Ionization Study” Interim Engineering,

Report No. 5, Index No ME-111273. Available from Naval Sea Systems Command

Technical Library, Code SEA 09B 312, National Center 3, Washington, DC

20362-5101.

11

If the liquid immersion medium is a low loss material, the

criterion simpliﬁes to

Em´8m . Es´8s =Ds 2 1 1

(X1.2)

and if the liquid immersion medium is a semiconducting

material the criterion becomes

E msm . 2pf´r ´0Es

(X1.3)

where:

E= electric strength,

f= frequency,

´ and ´8 = permittivity,

D= dissipation factor, and

s= conductivity (S/m).

Subscripts:

m refers to immersion medium,

r refers to relative,

0 refers to free space,

(´0 = 8.854 3 10 −12 F/m) and

s refers to solid dielectric.

Whitehead, S., Dielectric Breakdown of Solids, Oxford University Press,

1951.

10

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

D149 – 09

X1.5.2 The dielectric breakdown test may be used as a

material inspection or quality control test, as a means of

inferring other conditions such as variability, or to indicate

deteriorating processes such as thermal aging. In these uses of

the test it is the relative value of the breakdown voltage that is

important rather than the absolute value.

X2. STANDARDS REFERRING TO TEST METHOD D149

X2.1 Introduction

X2.1.1 The listing of documents in this appendix provides

reference to a broad range of ASTM standards concerned with

determination of dielectric strength at power frequencies or

with elements of test equipment or elements of procedural

details used to determine this property. While every effort has

been made to include as many as possible of the standards

referring to Test Method D149, the list may not be complete,

and standards written or revised after publication of this

appendix are not included.

X2.1.2 In some standards which specify that the dielectric

strength or the breakdown voltage is to be determined in

accordance with Test Method D149, the manner in which the

reference is made to this test method is not completely in

conformance with the requirements of 5.5. Do not use another

document, including those listed in this appendix, as a model

for reference to this test method unless there is conformity with

5.5.

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

D149 – 09

TABLE X2.1 ASTM Standards Referring to Test Method D149

ASTM Designation

Volume

Type of Standard

Subject

Thin Electrical Insulating Materials, Proof Tests

Detection and Measurement of Partial Discharge Pulses

Selection of Specimens and Test Parameters for International Commerce

Voltage Endurance with Partial Discharges on the Surface

Thermal Endurance, Rigid Insulating Materials

Thermal Failure Under Electrical Stress

Measurement of Energy and Charge Transfer Due to Partial Discharges

Dielectric Strength Using Impulse Waves

Dielectric Strength Using Direct Voltage

Electrical Breakdown by Treeing

Specifying Materials for Ionizing Radiation

Friction Tape

Untreated Insulating Paper

Varnished Cotton Fabric Tape

Black Bias-Cut Varnished Cloth and Tape

Vulcanized Fibre

Resin-Coated Glass Fabrics and Tapes

Pressure-Sensitive Tapes

Silicone Rubber Coated Glass Fabric and Tape

Silicone Varnished Glass Cloth and Tape

Flexible Materials, Thermal Endurance, Curved Electrode Method

Bondable Rubber Tapes

Polymeric Films

Flexible Composites

Impregnated Paper and Board

PTFE Resin Skived Tape

FEP Fluorocarbon Resin Sheet and Film

PTFE Resin Cast Film

Polyethylene Terephthalate Film

Semiconducting and Insulating Rubber Tapes

PTFE Coated Glass Fabric

Polyimide Resin Films

Melamine-Formaldehyde Molding Compounds

Urea-Formaldehyde Molding Compounds

Vinylidine Chloride Molding Compounds

Polychloroﬂuoroethylene (PCTFE) Plastics

Allyl Molding Compounds

Epoxy Molding Compounds

Poly(Vinylidene Fluoride) Molding, Extrusion, Coating Materials

High-Density Rigid Cellular Thermoplastics

Polycarbonate Materials

System for Specifying Plastics

Nylon Injection and Extrusion Materials

Polyphenylene Sulﬁde Injection and Extrusion Materials

High-Density Rigid Cellular Thermosets

Vitriﬁed Ceramic Materials

Pasted Mica

Natural Block Mica

Glass-Bonded Mica

Untreated Mica Paper

Alumina Ceramics

Rigid Sheet and Plate Materials

Laminated Tubes

Laminated Round Rods

Flexible Treated Sleeving

Laminated Thermosetting Materials

Nonrigid Vinyl Chloride Polymer Tubing

TFE Fluorocarbon Tubing

TFE Fluorocarbon Rod

Heat-Shrinkable Tubing

PTFE Molded Sheet

PTFE Molded Basic Shapes

PTFE Tubing

FEP Fluorocarbon Tubing

Insulating Board (Pressboard)

Liquid and Sheet Linings

General Standards not Speciﬁc to a Material or Material Class:

D138910.01Test Method

D186810.01Test Method

D199908.02Guide

D227510.01Test Method

D230410.01Test Method

D315110.02Test Method

10.02Test MethodD3382

D342610.02Test Method

D375510.02Test Method

D275610.02Test Method

E142012.02Guide

Fabric, Fiber, Paper, Tape, Film, Flexible Composites, and Coated Fabrics:

D6910.01Test Method

D20210.01Test Method

D29510.01Test Method

D37310.01Speciﬁcation

D61910.01Test Method

D90210.01Test Method

D100010.01Test Method

D145810.01Test Method

D145910.01Speciﬁcation

D183010.01Test Method

D214810.01Test Method

D230510.01Test Method

D238110.01Test Method

D241310.01Test Method

08.03SpeciﬁcationD3308

D336808.03Speciﬁcation

D336908.03Speciﬁcation

D366410.02Speciﬁcation

D432510.02Test Method

D496908.03Speciﬁcation

D521410.02Test Method

Polymeric Molding and Embedding Compounds:

D70408.01Speciﬁcation

D70508.01Speciﬁcation

D72908.01Speciﬁcation

D143008.01Speciﬁcation

D163608.02Speciﬁcation

D301308.02Speciﬁcation

D322208.03Speciﬁcation

D374808.03Practice

08.03SpeciﬁcationD3935

D400008.03Classiﬁcation

D406608.03Speciﬁcation

D406708.03Speciﬁcation

D409808.03Practice

Mica, Glass, and Porcelain:

D11610.01Test Method

D35210.01Test Method

D74810.01Speciﬁcation

D103910.01Test Method

D167710.01Test Method

D244215.02Speciﬁcation

Sleeving, Tubes, Sheets, and Rods:

D22910.01Test Method

D34810.01Test Method

D34910.01Test Method

D35010.01Test Method

D70910.01Speciﬁcation

D87610.01Test Method

D167510.01Test Method

D171010.01Speciﬁcation

D267110.02Test Method

D329308.03Speciﬁcation

D329408.03Speciﬁcation

D329508.03Speciﬁcation

D329608.03Speciﬁcation

D339410.02Speciﬁcation

D478706.01Practice

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758

D149 – 09

TABLE X2.1 Continued

ASTM Designation

Volume

Type of Standard

Subject

Reinforced Thermosetting Plastic Poles

Varnishes

Thermal Endurance, Flexible Varnishes

Insulating Gasses

Coating Powders and Their Coatings

Solventless Varnishes

Rubber

Rubber

Rubber

Rubber

Rubber

Rubber

Insulating

Insulating

Insulating

Insulating

Insulating

Insulating

Gloves

Matting

Blankets

Covers

Line Hose

Sleeves

D492308.03Speciﬁcation

Varnishes, Coatings, Insulating Fluids and Gasses, and Solvents:

D11510.01Test Method

D193210.01Test Method

D247710.03Test Method

D321410.02Test Method

D473310.02Test Method

Rubber and Rubber Products:

D12010.03Speciﬁcation

D17810.03Speciﬁcation

D104810.03Speciﬁcation

D104910.03Speciﬁcation

D105010.03Speciﬁcation

D105110.03Speciﬁcation

Filling Compounds:

D17610.01Test Method

Adhesives:

D130415.06Test Method

Wire and Cable Insulation:

D47010.01Test Method

D167610.01Test Method

D230710.01Test Method

D263310.02Test Method

D303210.02Test Method

D335310.02Test Method

Solid Filling and Treating Compounds

Adhesives Relative to Use as Electrical Insulation

Cross-Linked Insulation and Jackets for Wire and Cable

Film Insulation on Magnet Wire

Film Insulation on Magnetic Wire, Thermal Endurance

Thermoplastic Insulation and Jackets for Wire and Cable

Hookup Wire Insulation

Fibrous Insulation on Magnet Wire

SUMMARY OF CHANGES

Committee D09 has identiﬁed the location of selected changes to this test method since the last issue,

D149 – 97a(2004), that may impact the use of this test method. (Approved October 1, 2009)

(1) The standard was revised throughout to remove non-

mandatory language.

ASTM International takes no position respecting the validity of any patent rights asserted in connection with any item mentioned

in this standard. Users of this standard are expressly advised that determination of the validity of any such patent rights, and the risk

of infringement of such rights, are entirely their own responsibility.

This standard is subject to revision at any time by the responsible technical committee and must be reviewed every ﬁve years and

if not revised, either reapproved or withdrawn. Your comments are invited either for revision of this standard or for additional standards

and should be addressed to ASTM International Headquarters. Your comments will receive careful consideration at a meeting of the

responsible technical committee, which you may attend. If you feel that your comments have not received a fair hearing you should

make your views known to the ASTM Committee on Standards, at the address shown below.

This standard is copyrighted by ASTM International, 100 Barr Harbor Drive, PO Box C700, West Conshohocken, PA 19428-2959,

United States. Individual reprints (single or multiple copies) of this standard may be obtained by contacting ASTM at the above

address or at 610-832-9585 (phone), 610-832-9555 (fax), or service@astm.org (e-mail); or through the ASTM website

(www.astm.org).

长  春  恒  越  电  子  科  技  有  限  公  司

www.jlhykj.com 0431-86796799   www.jlhydz.net 0431-86796758